## 3ton
Entering Wet Bulb Temperature | Total Air Volume
|  | 85° F |  |  |  |  | 95° F |  |  |  |  | 105° F |  |  |  |  | 115° F |  |  |  |  | 125° F
|  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T)
|  |  |  | ----------------------- |  |  |  |  | ----------------------- |  |  |  |  | ----------------------- |  |  |  |  | ----------------------- |  |  |  |  | -----------------------
|  |  |  | Dry Bulb |  |  |  |  | Dry Bulb |  |  |  |  | Dry Bulb |  |  |  |  | Dry Bulb |  |  |  |  | Dry Bulb
| cfm | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F
59° F | 1075 | 35.4 | 2.01 | 0.92 | 1 | 1 | 34.2 | 2.26 | 0.94 | 1 | 1 | 32.8 | 2.54 | 0.96 | 1 | 1 | 31.2 | 2.87 | 0.99 | 1 | 1 | 29.4 | 3.25 | 1 | 1 | 1
| 1210 | 36.8 | 2.02 | 0.96 | 1 | 1 | 35.6 | 2.26 | 0.98 | 1 | 1 | 34.2 | 2.55 | 1 | 1 | 1 | 32.6 | 2.88 | 1 | 1 | 1 | 30.4 | 3.25 | 1 | 1 | 1
| 1370 | 38.5 | 2.03 | 0.99 | 1 | 1 | 37 | 2.27 | 1 | 1 | 1 | 35.6 | 2.56 | 1 | 1 | 1 | 33.8 | 2.88 | 1 | 1 | 1 | 31.6 | 3.26 | 1 | 1 | 1
63° F | 1075 | 36.8 | 2.01 | 0.75 | 0.88 | 1 | 35.4 | 2.26 | 0.77 | 0.9 | 1 | 33.8 | 2.55 | 0.78 | 0.93 | 1 | 31.8 | 2.88 | 0.8 | 0.96 | 1 | 29.4 | 3.25 | 0.83 | 0.99 | 1
| 1210 | 38 | 2.02 | 0.78 | 0.92 | 1 | 36.4 | 2.27 | 0.79 | 0.94 | 1 | 34.6 | 2.55 | 0.81 | 0.96 | 1 | 32.6 | 2.88 | 0.83 | 0.99 | 1 | 30.4 | 3.25 | 0.86 | 1 | 1
| 1370 | 39 | 2.03 | 0.8 | 0.96 | 1 | 37.4 | 2.27 | 0.82 | 0.98 | 1 | 35.6 | 2.56 | 0.84 | 1 | 1 | 33.8 | 2.88 | 0.87 | 1 | 1 | 31.6 | 3.26 | 0.9 | 1 | 1
67° F | 1075 | 39 | 2.03 | 0.6 | 0.73 | 0.85 | 37.4 | 2.27 | 0.6 | 0.74 | 0.87 | 35.8 | 2.56 | 0.62 | 0.75 | 0.89 | 33.8 | 2.89 | 0.63 | 0.78 | 0.92 | 31.2 | 3.25 | 0.64 | 0.8 | 0.96
| 1210 | 40 | 2.04 | 0.61 | 0.75 | 0.88 | 38.5 | 2.28 | 0.62 | 0.77 | 0.9 | 36.8 | 2.56 | 0.63 | 0.78 | 0.93 | 34.6 | 2.88 | 0.65 | 0.8 | 0.96 | 32.2 | 3.26 | 0.67 | 0.84 | 0.99
| 1370 | 41.5 | 2.05 | 0.63 | 0.78 | 0.92 | 39.5 | 2.29 | 0.64 | 0.79 | 0.94 | 37.8 | 2.57 | 0.65 | 0.81 | 0.97 | 35.6 | 2.89 | 0.67 | 0.84 | 1 | 32.8 | 3.26 | 0.69 | 0.87 | 1
71° F | 1075 | 41 | 2.04 | 0.46 | 0.58 | 0.7 | 39.5 | 2.29 | 0.46 | 0.59 | 0.71 | 37.6 | 2.57 | 0.47 | 0.6 | 0.73 | 35.4 | 2.89 | 0.47 | 0.61 | 0.75 | 33 | 3.26 | 0.48 | 0.63 | 0.77
| 1210 | 42 | 2.05 | 0.47 | 0.6 | 0.72 | 40.5 | 2.29 | 0.47 | 0.61 | 0.74 | 38.5 | 2.57 | 0.48 | 0.62 | 0.76 | 36.4 | 2.9 | 0.48 | 0.63 | 0.78 | 33.8 | 3.26 | 0.49 | 0.65 | 0.81
| 1370 | 43.5 | 2.06 | 0.48 | 0.62 | 0.75 | 41.5 | 2.3 | 0.48 | 0.63 | 0.77 | 39.5 | 2.57 | 0.49 | 0.64 | 0.79 | 37.4 | 2.89 | 0.5 | 0.65 | 0.81 | 34.8 | 3.27 | 0.51 | 0.68 | 0.84

## 2.5ton
Entering Wet Bulb Temperature | Total Air Volume
|  | 85° F |  |  |  |  | 95° F |  |  |  |  | 105° F |  |  |  |  | 115° F |  |  |  |  | 125° F
|  | Total Cool Cap. | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap. | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap. | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap. | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap. | Comp Motor Input | Sensible to Total Ratio (S/T)
|  |  |  | ----------------------- |  |  |  |  | ----------------------- |  |  |  |  | ----------------------- |  |  |  |  | ----------------------- |  |  |  |  | -----------------------
|  |  |  | Dry Bulb |  |  |  |  | Dry Bulb |  |  |  |  | Dry Bulb |  |  |  |  | Dry Bulb |  |  |  |  | Dry Bulb
| cfm | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F
59° F | 930 | 27.4 | 1.54 | 0.96 | 1 | 1 | 26.2 | 1.74 | 0.98 | 1 | 1 | 25 | 1.99 | 1 | 1 | 1 | 23.8 | 2.27 | 1 | 1 | 1 | 22.2 | 2.62 | 1 | 1 | 1
| 980 | 27.8 | 1.53 | 0.98 | 1 | 1 | 26.6 | 1.74 | 1 | 1 | 1 | 25.4 | 1.99 | 1 | 1 | 1 | 24 | 2.27 | 1 | 1 | 1 | 22.6 | 2.62 | 1 | 1 | 1
| 1115 | 28.8 | 1.53 | 1 | 1 | 1 | 27.6 | 1.74 | 1 | 1 | 1 | 26.4 | 1.99 | 1 | 1 | 1 | 25 | 2.28 | 1 | 1 | 1 | 23.2 | 2.61 | 1 | 1 | 1
63° F | 930 | 28.2 | 1.53 | 0.78 | 0.93 | 1 | 26.8 | 1.74 | 0.8 | 0.95 | 1 | 25.4 | 1.99 | 0.82 | 0.98 | 1 | 23.8 | 2.27 | 0.84 | 1 | 1 | 22.2 | 2.62 | 0.88 | 1 | 1
| 980 | 28.4 | 1.53 | 0.79 | 0.94 | 1 | 27 | 1.74 | 0.81 | 0.97 | 1 | 25.6 | 1.98 | 0.83 | 0.99 | 1 | 24 | 2.28 | 0.86 | 1 | 1 | 22.6 | 2.61 | 0.9 | 1 | 1
| 1115 | 29.2 | 1.53 | 0.82 | 0.98 | 1 | 27.8 | 1.74 | 0.85 | 1 | 1 | 26.4 | 1.99 | 0.87 | 1 | 1 | 25 | 2.27 | 0.9 | 1 | 1 | 23.4 | 2.61 | 0.94 | 1 | 1
67° F | 930 | 29.8 | 1.53 | 0.61 | 0.75 | 0.89 | 28.4 | 1.74 | 0.62 | 0.77 | 0.92 | 26.8 | 1.99 | 0.64 | 0.79 | 0.94 | 25.2 | 2.27 | 0.65 | 0.82 | 0.98 | 23.2 | 2.61 | 0.67 | 0.86 | 1
| 980 | 30 | 1.53 | 0.62 | 0.77 | 0.91 | 28.6 | 1.74 | 0.63 | 0.78 | 0.93 | 27 | 1.98 | 0.64 | 0.81 | 0.96 | 25.4 | 2.27 | 0.66 | 0.84 | 0.99 | 23.4 | 2.61 | 0.68 | 0.87 | 1
| 1115 | 30.8 | 1.53 | 0.64 | 0.8 | 0.95 | 29.2 | 1.74 | 0.65 | 0.82 | 0.98 | 27.6 | 1.98 | 0.67 | 0.85 | 1 | 25.8 | 2.27 | 0.69 | 0.88 | 1 | 23.8 | 2.62 | 0.72 | 0.92 | 1
71° F | 930 | 31.4 | 1.53 | 0.46 | 0.6 | 0.73 | 30 | 1.74 | 0.47 | 0.61 | 0.75 | 28.4 | 1.98 | 0.47 | 0.62 | 0.77 | 26.6 | 2.27 | 0.48 | 0.64 | 0.8 | 24.6 | 2.61 | 0.49 | 0.66 | 0.83
| 980 | 31.8 | 1.53 | 0.47 | 0.61 | 0.74 | 30.2 | 1.74 | 0.47 | 0.62 | 0.76 | 28.6 | 1.98 | 0.48 | 0.63 | 0.79 | 26.8 | 2.27 | 0.49 | 0.65 | 0.81 | 25 | 2.61 | 0.5 | 0.67 | 0.85
| 1115 | 32.4 | 1.53 | 0.48 | 0.63 | 0.78 | 31 | 1.74 | 0.48 | 0.64 | 0.8 | 29.2 | 1.98 | 0.49 | 0.66 | 0.82 | 27.4 | 2.27 | 0.5 | 0.68 | 0.85 | 25.4 | 2.61 | 0.51 | 0.71 | 0.9

## 2ton
ntering Wet Bulb Temperature | Total Air Volume
|  | 85° F |  |  |  |  | 95° F |  |  |  |  | 105° F |  |  |  |  | 115° F |  |  |  |  | 125° F
|  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T)
|  |  |  | ----------------------- |  |  |  |  | ----------------------- |  |  |  |  | ----------------------- |  |  |  |  | ----------------------- |  |  |  |  | -----------------------
|  |  |  | Dry Bulb |  |  |  |  | Dry Bulb |  |  |  |  | Dry Bulb |  |  |  |  | Dry Bulb |  |  |  |  | Dry Bulb
| cfm | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F
59° F | 720 | 23.8 | 1.33 | 0.93 | 1 | 1 | 22.8 | 1.49 | 0.95 | 1 | 1 | 21.8 | 1.68 | 0.98 | 1 | 1 | 20.6 | 1.91 | 1 | 1 | 1 | 19.4 | 2.18 | 1 | 1 | 1
| 815 | 24.6 | 1.33 | 0.97 | 1 | 1 | 23.8 | 1.49 | 0.99 | 1 | 1 | 22.6 | 1.68 | 1 | 1 | 1 | 21.4 | 1.91 | 1 | 1 | 1 | 20.2 | 2.18 | 1 | 1 | 1
| 905 | 25.4 | 1.33 | 0.99 | 1 | 1 | 24.4 | 1.5 | 1 | 1 | 1 | 23.4 | 1.69 | 1 | 1 | 1 | 22.2 | 1.91 | 1 | 1 | 1 | 20.8 | 2.19 | 1 | 1 | 1
63° F | 720 | 24.4 | 1.33 | 0.76 | 0.9 | 1 | 23.4 | 1.49 | 0.78 | 0.92 | 1 | 22.2 | 1.68 | 0.79 | 0.95 | 1 | 20.8 | 1.91 | 0.82 | 0.97 | 1 | 19.4 | 2.18 | 0.85 | 1 | 1
| 815 | 25.2 | 1.33 | 0.79 | 0.93 | 1 | 24 | 1.5 | 0.8 | 0.96 | 1 | 22.8 | 1.68 | 0.82 | 0.98 | 1 | 21.4 | 1.91 | 0.85 | 1 | 1 | 20.2 | 2.18 | 0.88 | 1 | 1
| 905 | 25.8 | 1.33 | 0.81 | 0.97 | 1 | 24.6 | 1.5 | 0.83 | 0.99 | 1 | 23.4 | 1.69 | 0.85 | 1 | 1 | 22.2 | 1.91 | 0.88 | 1 | 1 | 20.8 | 2.19 | 0.92 | 1 | 1
67° F | 720 | 25.6 | 1.33 | 0.6 | 0.74 | 0.86 | 24.4 | 1.5 | 0.61 | 0.75 | 0.89 | 23.2 | 1.69 | 0.62 | 0.77 | 0.91 | 22 | 1.91 | 0.64 | 0.79 | 0.94 | 20.4 | 2.18 | 0.66 | 0.82 | 0.97
| 815 | 26.4 | 1.34 | 0.62 | 0.76 | 0.9 | 25.2 | 1.5 | 0.63 | 0.78 | 0.92 | 24 | 1.69 | 0.64 | 0.8 | 0.95 | 22.4 | 1.91 | 0.66 | 0.83 | 0.98 | 21 | 2.19 | 0.68 | 0.86 | 1
| 905 | 27 | 1.34 | 0.64 | 0.79 | 0.93 | 25.8 | 1.5 | 0.65 | 0.81 | 0.96 | 24.4 | 1.69 | 0.66 | 0.83 | 0.98 | 22.8 | 1.91 | 0.68 | 0.86 | 1 | 21.4 | 2.19 | 0.7 | 0.89 | 1
71° F | 720 | 26.8 | 1.34 | 0.46 | 0.59 | 0.71 | 25.6 | 1.5 | 0.47 | 0.6 | 0.73 | 24.4 | 1.69 | 0.47 | 0.61 | 0.74 | 23 | 1.92 | 0.48 | 0.62 | 0.77 | 21.4 | 2.19 | 0.48 | 0.64 | 0.79
| 815 | 27.6 | 1.34 | 0.47 | 0.61 | 0.74 | 26.4 | 1.51 | 0.47 | 0.62 | 0.76 | 25 | 1.69 | 0.48 | 0.63 | 0.77 | 23.6 | 1.92 | 0.49 | 0.65 | 0.8 | 22 | 2.19 | 0.5 | 0.67 | 0.83
| 905 | 28.2 | 1.35 | 0.48 | 0.62 | 0.76 | 27 | 1.51 | 0.48 | 0.64 | 0.78 | 25.6 | 1.7 | 0.49 | 0.65 | 0.8 | 24 | 1.92 | 0.5 | 0.67 | 0.83 | 22.4 | 2.2 | 0.51 | 0.69 | 0.86

## 4ton
Entering Wet Bulb Temperature | Total Air Volume
|  | 85° F |  |  |  |  | 95° F |  |  |  |  | 105° F |  |  |  |  | 115° F |  |  |  |  | 125° F
|  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T) |  |  | Total Cool Cap | Comp Motor Input | Sensible to Total Ratio (S/T)
|  |  |  | ----------------------- |  |  |  |  | ----------------------- |  |  |  |  | ----------------------- |  |  |  |  | ----------------------- |  |  |  |  | -----------------------
|  |  |  | Dry Bulb |  |  |  |  | Dry Bulb |  |  |  |  | Dry Bulb |  |  |  |  | Dry Bulb |  |  |  |  | Dry Bulb
| cfm | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F | kBtuh | kW | 75° F | 80° F | 85° F
59° F | 1350 | 44 | 2.63 | 0.91 | 1 | 1 | 42 | 2.97 | 0.93 | 1 | 1 | 40.5 | 3.38 | 0.95 | 1 | 1 | 38 | 3.85 | 0.99 | 1 | 1 | 36 | 4.43 | 1 | 1 | 1
| 1590 | 46.5 | 2.65 | 0.95 | 1 | 1 | 44.5 | 3 | 0.98 | 1 | 1 | 42.5 | 3.4 | 1 | 1 | 1 | 40.5 | 3.88 | 1 | 1 | 1 | 37.8 | 4.46 | 1 | 1 | 1
| 1590 | 46.5 | 2.65 | 0.95 | 1 | 1 | 44.5 | 3 | 0.98 | 1 | 1 | 42.5 | 3.4 | 1 | 1 | 1 | 40.5 | 3.88 | 1 | 1 | 1 | 37.8 | 4.46 | 1 | 1 | 1
63° F | 1350 | 46 | 2.64 | 0.74 | 0.87 | 0.99 | 44 | 2.99 | 0.76 | 0.89 | 1 | 41.5 | 3.39 | 0.77 | 0.92 | 1 | 39 | 3.86 | 0.8 | 0.95 | 1 | 36.4 | 4.43 | 0.82 | 0.98 | 1
| 1590 | 48 | 2.66 | 0.77 | 0.92 | 1 | 45.5 | 3 | 0.79 | 0.94 | 1 | 43 | 3.41 | 0.81 | 0.97 | 1 | 40.5 | 3.88 | 0.84 | 1 | 1 | 38 | 4.46 | 0.87 | 1 | 1
| 1590 | 48 | 2.66 | 0.77 | 0.92 | 1 | 45.5 | 3 | 0.79 | 0.94 | 1 | 43 | 3.41 | 0.81 | 0.97 | 1 | 40.5 | 3.88 | 0.84 | 1 | 1 | 38 | 4.46 | 0.87 | 1 | 1
67° F | 1350 | 48.5 | 2.66 | 0.6 | 0.72 | 0.84 | 46 | 3.01 | 0.6 | 0.73 | 0.86 | 43.5 | 3.41 | 0.61 | 0.75 | 0.88 | 41.5 | 3.89 | 0.62 | 0.77 | 0.91 | 38.5 | 4.47 | 0.64 | 0.8 | 0.95
| 1590 | 50 | 2.68 | 0.62 | 0.75 | 0.88 | 48 | 3.02 | 0.62 | 0.77 | 0.91 | 45.5 | 3.43 | 0.64 | 0.79 | 0.93 | 42.5 | 3.91 | 0.65 | 0.81 | 0.97 | 40 | 4.49 | 0.67 | 0.84 | 1
| 1590 | 50 | 2.68 | 0.62 | 0.75 | 0.88 | 48 | 3.02 | 0.62 | 0.77 | 0.91 | 45.5 | 3.43 | 0.64 | 0.79 | 0.93 | 42.5 | 3.91 | 0.65 | 0.81 | 0.97 | 40 | 4.49 | 0.67 | 0.84 | 1
71° F | 1350 | 51 | 2.68 | 0.46 | 0.58 | 0.69 | 48.5 | 3.03 | 0.46 | 0.59 | 0.71 | 46.5 | 3.44 | 0.47 | 0.6 | 0.72 | 43.5 | 3.92 | 0.47 | 0.61 | 0.74 | 41 | 4.5 | 0.48 | 0.63 | 0.77
| 1590 | 52.5 | 2.69 | 0.47 | 0.6 | 0.73 | 50 | 3.04 | 0.48 | 0.61 | 0.74 | 47.5 | 3.46 | 0.48 | 0.62 | 0.76 | 45 | 3.94 | 0.49 | 0.64 | 0.79 | 42 | 4.52 | 0.5 | 0.66 | 0.82
| 1590 | 52.5 | 2.69 | 0.47 | 0.6 | 0.73 | 50 | 3.04 | 0.48 | 0.61 | 0.74 | 47.5 | 3.46 | 0.48 | 0.62 | 0.76 | 45 | 3.94 | 0.49 | 0.64 | 0.79 | 42 | 4.52 | 0.5 | 0.66 | 0.82